## Flow Calculation
https://www.gustavopreston.com/
Syncroflo Booster Calculator
Project: |  |  | Location |  |  |  | Page: | 1 | 800 gpm or higher use a Quadraplex
Subject: | SFI Booster |  | Calc. By: |  |  |  | Date: |  | 250 –800 gpm use a Triplex
Engineer |  |  | Checked By: |  |  |  | Date: |  | 250 gpm or less use a Duplex
Pumps Splits as a percentage of total flow required.
B: Fixture Flow Units: | [8 empty] | * 50/50
If a booster system is required, use this form to determine peak flow capacity. Do not include | [8 empty] | * 65/65 – most common
fixtures handled by city pressure (lower floors). | [8 empty] | * 80/80 – most common
|  |  |  | QTY |  | SFU |  | EXTENSION | * 100/100
Aspirator |  |  |  | 0 |  | 2 |  | 0 | * 20/40/40
Autopsy Table, Complete |  |  |  | 0 |  | 3 |  | 0 | * 33/33/33
Autopsy Table, Aspriator |  |  |  | 0 |  | 2 |  | 0 | * 50/50/50 – most common
Autopsy Table, Flushing Hose |  |  |  | 0 |  | 2 |  | 0 | * 25/25/25/25
Autopsy Table, Flushing Rim |  |  |  | 0 |  | 3 |  | 0
Autopsy Table, Sink Faucet |  |  |  | 0 |  | 2.5 |  | 0
Autopsy Table, Waste Disposal |  |  |  | 0 |  | 1.5 |  | 0 | http://www.pumpsebara.com/pump-selector/selector/ | Ebara Sizing
Bath, Arm |  |  |  | 0 |  | 2 |  | 0
Bath, Emergency |  |  |  | 0 |  | 2 |  | 0 | https://pumpselection.spppumps.com/ | Kirloskar Sizing - Intelliquip
Bath, Immersion |  |  |  | 0 |  | 7 |  | 0
Bath, Leg |  |  |  | 0 |  | 4 |  | 0 | http://extranet.syncroflo.com/quote--order-entry/quote-request-form.aspx | Syncroflo Quote Request Form
Bath, Sitz |  |  |  | 0 |  | 2 |  | 0
Bathroom Group - Flush Valve |  |  |  | 0 |  | 8 |  | 0
Bathroom Group - Flush Tank |  |  |  | 0 |  | 6 |  | 0
Bathtub |  |  |  | 0 |  | 5 |  | 0
Bedpan Washer, Steam |  |  |  | 0 |  | 10 |  | 0
Bidet |  |  |  | 0 |  | 3 |  | 0
Cleaner, Sonic |  |  |  | 0 |  | 2.5 |  | 0
Clothes Washer (private) |  |  |  | 0 |  | 2 |  | 0
Clothes Washer (public) |  |  |  | 0 |  | 4 |  | 0
Cuspidor, Dental and Surgical |  |  |  | 0 |  | 1 |  | 0
Cuspidor, Dental Chair |  |  |  | 0 |  | 1 |  | 0
Dishwasher |  |  |  | 0 |  | 6 |  | 0
Drinking Fountain |  |  |  | 0 |  | 2 |  | 0
Emergency Eyewash & Shower |  |  |  | 0 |  | 10 |  | 0
Emergency Eyewash Only |  |  |  | 2 max |  | 2 |  | 0
Floor Drain, Flushing Type |  |  |  | 0 |  | 10 |  | 0
Garbage Disposal, Sink |  |  |  | 0 |  | 3 |  | 0
Hose, Bed Pan General |  |  |  | 0 |  | 1.5 |  | 0
Hose, Bed Pan Private |  |  |  | 0 |  | 1
Kitchen Sink |  |  |  | 0 |  | 4 |  | 0
Laundry Tray (1 to 3) |  |  |  | 0 |  | 3 |  | 0
Lavatory, Barber |  |  |  | 0 |  | 1.5 |  | 0
Lavatory, Dental |  |  |  | 0 |  | 1
Lavatory, Nursery |  |  |  | 0 |  | 1.5 |  | 0
Lavatory - Private |  |  |  | 0 |  | 0.75 |  | 0
Lavatory - Public |  |  |  | 0 |  | 1.5 |  | 0
Lavatory, Scrub-up |  |  |  | 0 |  | 1.5
Labatory, Treatment |  |  |  | 0 |  | 1
Microscope, Electron |  |  |  | 0 |  | 1 |  | 0
Shower, Obstetrical |  |  |  | 0 |  | 2 |  | 0
Shower, Therapeutic |  |  |  | 0 |  | 6 |  | 0
Shower Stall - Private, Mixing Valve |  |  |  | 0 |  | 2 |  | 0
Shower Head - Public, Mixing Valve |  |  |  | 0 |  | 3 |  | 0
Sink, Animal Area |  |  |  | 0 |  | 2 |  | 0
Sink, Barium |  |  |  | 0 |  | 2.5 |  | 0
Sink, Central Supply |  |  |  | 0 |  | 2.5 |  | 0
Sink, Clean-up Room |  |  |  | 0 |  | 2.5 |  | 0
Sink, Clinical |  |  |  | 0 |  | 10 |  | 0
Sink, Clinical, Bed Pan Hose |  |  |  | 0 |  | 10 |  | 0
Sink, Cup |  |  |  | 0 |  | 1 |  | 0
Sink, Floor |  |  |  | 0 |  | 3 |  | 0
Sink, Formula Room |  |  |  | 0 |  | 3 |  | 0
Sink, Laboratory |  |  |  | 0 |  | 1.5 |  | 0
Sink, Laboratory and Trough |  |  |  | 0 |  | 2.5 |  | 0
Sink, Mop |  |  |  | 0 |  | 3 |  | 0
Sink, Pharmacy |  |  |  | 0 |  | 1.5 |  | 0
Sink, Plaster |  |  |  | 0 |  | 3 |  | 0
Sink, Nurse's Station |  |  |  | 0 |  | 1.5 |  | 0
Sink, Scrub-up |  |  |  | 0 |  | 3 |  | 0
Sink, Clean Utility |  |  |  | 0 |  | 2.5 |  | 0
Sink, Soiled Utility |  |  |  | 0 |  | 2.5 |  | 0
Sterilizer, Pressure Instrument |  |  |  | 0 |  | 2 |  | 0
Sterilizer, Water |  |  |  | 0 |  | 5 |  | 0
Urinal - Pedestal Flush Valve |  |  |  | 0 |  | 10 |  | 0
Uninal- Stall or Wall |  |  |  | 0 |  | 5 |  | 0
Washer, Sterilizer |  |  |  | 0 |  | 6 |  | 0
Washer, Formula Bottle |  |  |  | 0 |  | 4 |  | 0
Washer, Glove |  |  |  | 0 |  | 3 |  | 0
Washer,Needle |  |  |  | 0 |  | 2 |  | 0
Washer, Pipette |  |  |  | 0 |  | 3 |  | 0
Washer, Tube |  |  |  | 0 |  | 4 |  | 0
Washer, Sterlizer, Utensil |  |  |  | 0 |  | 1.5 |  | 0
Water Closet - Flush Tank |  |  |  | 0 |  | 5 |  | 0
Water Closet - Flush Valve |  |  |  | 0 |  | 10 |  | 0
Hose, Bibb, Interior |  |  |  | 0 |  | 4 |  | 0
Wall Hydrants |  |  |  | 0 |  | 2 |  | 0
ice makers |  |  |  | 0 |  | 3 |  | 0
Other Load_____________________ | [7 empty] | 0
0
Continuous Flow |  |  |  |  | Total FU |  |  | 0
| Other Flow | @ GPM
| Other Flow | @ GPM |  |  | Sub-Total GPM |  |  | 65
| TONS AC | @ 0.1 GPM/TON |  | 0
| HP | @ 1 GPM/HP |  | 0 |  | Total GPM |  | 65
Input Velocity | [5 empty] | Flow in CFS |  | 0.14495
(Suggest 5-8 FPS)
|  | FPS |  |  | Pipe Size (In) |  |  | 0
Modified FU to GPM CALC FROM MODIFIED HUNTERS |  |  |  |  | Friction Loss (PSI/FT) |  |  | 0
High F.U. = | Apt./Office300 | 300 | Select from total system Peak Flow
Low F.U. = | Apt./Office100 | 100 | Select from total system Peak Flow |  |  |  |  | Select high and low fixture counts using the building type
High GPM = | 80 |  | Select from total system Peak Flow
Low GPM = | 70 |  | Select from total system Peak Flow
Calculated F.U. = | 0 |  | Select from total system Peak Flow
Unknown Flow = X | 65 |  | Enter this value in SubTotal GPM above
FU Difference | 200 | -100 | Calc FU Minus Low FU
GPM Difference | 10 | -5 | Calc GPM as a ration of Calc FU divided by FU Differential time GPM Difference
Total SYSTEM Peak Flow (GPM)
| Fixture Flow units |  |  | Apt./Office |  | Hotel |  | Hospital
| 100 |  |  | 70 |  | 80 |  | 100
| 300 |  |  | 80 |  | 90 |  | 100
| 600 |  |  | 100 |  | 100 |  | 120
| 900 |  |  | 120 |  | 125 |  | 135
| 1200 |  |  | 135 |  | 145 |  | 155
| 1500 |  |  | 150 |  | 165 |  | 185
| 1750 |  |  | 170 |  | 185 |  | 200
| 2000 |  |  | 190 |  | 200 |  | 220
| 3000 |  |  | 250 |  | 275 |  | 300
| 4000 |  |  | 300 |  | 340 |  | 365
| 5000 |  |  | 350 |  | 400 |  | 430
| 6000 |  |  | 400 |  | 450 |  | 490
| 7000 |  |  | 450 |  | 500 |  | 540
| 8000 |  |  | 490 |  | 550 |  | 600

## System GPM load (hidden)
Total SYSTEM Peak Flow (GPM)
Fixture Flow units |  | Apt./Office | Hotel | Hospital | Apt./Office | Fixture Flow units |  | GPM
[5 empty] | Apt./Office | 100 | Apt./Office100 | 70 | 100
100 |  | 70 | 80 | 100 | Apt./Office | 300 | Apt./Office300 | 80 | 300
300 |  | 80 | 90 | 100 | Apt./Office | 600 | Apt./Office600 | 100 | 600
600 |  | 100 | 100 | 120 | Apt./Office | 900 | Apt./Office900 | 120 | 900
900 |  | 120 | 125 | 135 | Apt./Office | 1200 | Apt./Office1200 | 135 | 1200
[5 empty] | Apt./Office | 1500 | Apt./Office1500 | 150 | 1500
1200 |  | 135 | 145 | 155 | Apt./Office | 1750 | Apt./Office1750 | 170 | 1750
1500 |  | 150 | 165 | 185 | Apt./Office | 2000 | Apt./Office2000 | 190 | 2000
1750 |  | 170 | 185 | 200 | Apt./Office | 3000 | Apt./Office3000 | 250 | 3000
2000 |  | 190 | 200 | 220 | Apt./Office | 4000 | Apt./Office4000 | 300 | 4000
[5 empty] | Apt./Office | 5000 | Apt./Office5000 | 350 | 5000
3000 |  | 250 | 275 | 300 | Apt./Office | 6000 | Apt./Office6000 | 400 | 6000
4000 |  | 300 | 340 | 365 | Apt./Office | 7000 | Apt./Office7000 | 450 | 7000
5000 |  | 350 | 400 | 430 | Apt./Office | 8000 | Apt./Office8000 | 490 | 8000
6000 |  | 400 | 450 | 490 | Hotel | 100 | Hotel100 | 80 | 100
7000 |  | 450 | 500 | 540 | Hotel | 300 | Hotel300 | 90 | 300
8000 |  | 490 | 550 | 600 | Hotel | 600 | Hotel600 | 100 | 600
[5 empty] | Hotel | 900 | Hotel900 | 125 | 900
[5 empty] | Hotel | 1200 | Hotel1200 | 145 | 1200
[5 empty] | Hotel | 1500 | Hotel1500 | 165 | 1500
[5 empty] | Hotel | 1750 | Hotel1750 | 185 | 1750
[5 empty] | Hotel | 2000 | Hotel2000 | 200 | 2000
[5 empty] | Hotel | 3000 | Hotel3000 | 275 | 3000
[5 empty] | Hotel | 4000 | Hotel4000 | 340 | 4000
[5 empty] | Hotel | 5000 | Hotel5000 | 400 | 5000
[5 empty] | Hotel | 6000 | Hotel6000 | 450 | 6000
[5 empty] | Hotel | 7000 | Hotel7000 | 500 | 7000
[5 empty] | Hotel | 8000 | Hotel8000 | 550 | 8000
[5 empty] | Hospital | 100 | Hospital100 | 100 | 100
[5 empty] | Hospital | 300 | Hospital300 | 100 | 300
[5 empty] | Hospital | 600 | Hospital600 | 120 | 600
[5 empty] | Hospital | 900 | Hospital900 | 135 | 900
[5 empty] | Hospital | 1200 | Hospital1200 | 155 | 1200
[5 empty] | Hospital | 1500 | Hospital1500 | 185 | 1500
[5 empty] | Hospital | 1750 | Hospital1750 | 200 | 1750
[5 empty] | Hospital | 2000 | Hospital2000 | 220 | 2000
[5 empty] | Hospital | 3000 | Hospital3000 | 300 | 3000
[5 empty] | Hospital | 4000 | Hospital4000 | 365 | 4000
[5 empty] | Hospital | 5000 | Hospital5000 | 430 | 5000
[5 empty] | Hospital | 6000 | Hospital6000 | 490 | 6000
[5 empty] | Hospital | 7000 | Hospital7000 | 540 | 7000
[5 empty] | Hospital | 8000 | Hospital8000 | 600 | 8000

## Ebara Pump Sizing Link (hidden)
http://www.pumpsebara.com/pump-selector/selector/ |  | Ebara pump sizing
https://pumpselection.spppumps.com/ |  | Intelliquip Pump Sizing
rmerullo@gustavopreston.com
init